Please fill out and email / post back to Chris lamb - Manager Aviation Quality & Compliance

Christopher.lamb@ior.com.au or SMS 0418 150 928

| TANK ID NUNBER as on tank ……………… | Port ………. | Date ……….. |  | Contact details. Name:. Address:. Mobile Number –. Email Address –. Postal Address –. |
| --- | --- | --- | --- | --- |
| DESIGN FEATURE & EQUIPMENT |  |  |  |  |  |  |  |  |  |
| STORAGE TANKS Paint – General Condition (dirty in need of wash) Advise also if tank has any vegetation touching tank (grass / trees at acceptable height) |  |  |  |  |  |  |  |  | Acceptable NOT Acceptable |
| HAZCHEM Correct label for Fuel Grade 1203 3YE AVGAS 1863 3Y JET A1 HAZCHEM box on outside of gate Documents inside – Detailed Site map, Safety Data Sheets, Contact list (current) |  |  |  |  |  |  |  |  | Acceptable NOT Acceptable |
| START/STOP SWITCHES (CLEAR ID, ACCESS) – Clearly marked and red in colour not faded |  |  |  |  |  |  |  |  |  |
| APPLICABLE ID SIGNS- JET A1 / AVGAS storage and equipment Uplift points must be clearly marked with JET A1 decals / AVGAS No Smoking / No Mobile Phones / Nil Ignition Return Ladders to storage Spill Kit – Serviceable with correct contents or sealed |  |  |  |  |  |  |  |  | Acceptable NOT Acceptable |
| FUEL EQUIPMENT MARKINGS TO EI 1542 (correct decal) On pipelines or on display AVGAS 100LL– White stripe with Blue / Red background JET A1 – 2 white stripes on black background (White Lettering) |  |  |  |  |  |  |  |  | Acceptable NOT Acceptable |
| Fence / locks (combination) / Security General presentation / condition of site – Clean and tidy (nil FOD) Acceptable to customers |  |  |  |  |  |  |  |  | Acceptable NOT Acceptable |
| Ladders Condition - Suitability - Stored correctly – |  |  |  |  |  |  |  |  | Acceptable NOT Acceptable |
| Kubota Diesel Generator (if installed on site) Yes ………….. No………… Check Battery under load (use meter) and ensure battery passes load test. Check leads for tightness. Visual check of terminals – nil corrosion build up Record battery install date or DOM (replace if over 3years old) …/……. Check and clean solar panel (remove any dirt or dust) Record Solar voltage …………………………Volts |  |  |  |  |  |  |  |  | Acceptable NOT Acceptable |
| DESIGN of Tank |  |  |  |  | HORIZONTAL VERTICAL  |  |  |  |  |
| DATE OF LAST TANK CLEAN / INSPECTION - Displayed on tank INTERVAL: 12m Internal / External Inspection 3/5 Years – Clean Internal |  |  |  |  | Dates |
| TANK QC SAMPLING & PRODUCT RECOVERY SYSTEMS - Low Point sample QTY Decal – (QTY removed before live sample) Visijar (Clean) Cotton Cloth (Available) Box of Gloves -fuel grade (Available) JET A1 -Box of Shell CWD (in date) and or AVGAS -Paste (no exp date) Stainless Steel Bucket with earth lead attached. QC Cabinet Clean with no old CWD’s or used rags / rubbish inside |  |  |  |  |  | Acceptable NOT Acceptable Acceptable; NOT Acceptable. |
| TANK SUMP SAMPLE Clear and Bright – Water White (Any prior history of water RECORD ON QC SHEET) If required store sample - 24hours with correct label attached. Time, Date and Grade QC book 2024 – filled out correctly – any concerns recorded in book |  |  |  |  |  |  | Acceptable NOT Acceptable |
| FILTRATION – visual Only |  |  |  |  |  |  |  |  |  |
| FILTER TYPE Monitor Has filter got a Differential Pressure Gauge on top of vessel (DP) and its operational. DP working correctly and within green band |  |  | Acceptable NOT Acceptable |
| DATE ELEMENTS CHANGED (12m change out) Is there a decal with – Date - on side of vessel |  |  | FILTER NO.: Change out DATE: INTERVAL: |
| HOSE (CONDITION) Record – Date of Manufacture (stamped on hose 4-digit date) Hose reel – Manual / Auto operated – Handle Lubricated with grease and fully operational. Clean off access grease Hose end nozzle clearly displayed with Grade of fuel |  |  |  |  |  |  |  | Acceptable NOT Acceptable |
| FIRE EXTINGUISHERS (6m / 12m Tagged and tested) Date stamp - |  |  |  |  |  |  |  | Acceptable NOT Acceptable |
| Please take some photos if possible and include with this report Thanks you – and remember it’s your site….. |  |  |  |  |  |  |  |  |  |

Findings

Observations

Comments